## Inputs
Project Input Parameters | Values/Selection | Units | Notes for Values/Selection
Project Name
Project Category | GOLD 2
Project Location
Building Numbers Per Society | 2 | Nos
Building Input Parameters For 1 building | Values/Selection | Units | Notes for Values/Selection
General
Building Height | 90 | Mtr
No of Floors | 38 | Nos | Excluding Ground Floor, ie, if 38 floors then it is assumed that it is G+38
Floor to Floor Height | 2.37 | Mtr
Ground Floor Entrance Lobby | 100 | Sq.M
Typical Floor lift Lobby | 30 | Sq.M
Fire lift Lobby | 8 | Sq.M |  | Abbreviations & Notes
Terrace area | 800 | Sq.M |  | Project Level Data
Refuger Floor | 5 | Nos |  | Society level data
Refuger Floor Area | 90 | Sq.M |  | Building Leve Data
Landscape Area per tower | 500 | Sq.M | Podium tops, building periphery landscapes, walkways etc | Apartment Level Data
Service Floor | 1 | Nos
Service Floor Area | 1200 | Sq.M
Typical Floor Lobby Type | Nat. Vent
Fire lift Lobby Type | Nat. Vent
Staircase type for STR 1 | Nat. Vent
Staircase type for STR 2 | Nat. Vent
Lifts
No of Passenger only lifts | 2 | Nos
No of Pass. Lift in Fire case | 1 | Nos
No of Firemen Evac/Service/Strecher lift | 1 | Nos
HVAC & Ventilation
No. Of Fully Enclosed Wet Services Shaft with Single Toilet | 4 | Nos
No. Of Fully Enclosed Wet Services Shaft with Two Toilet | 2 | Nos
Number of Meter room at GF | 3 | Nos
Average Area of Meter room | 15 | Sq.m
Electrical Panel Room Area | 25 | Sq.m
IBS Room | 15 | Sq.m
OWC Room | 50 | Sq.m
FCC Room | 30 | Sq.m
Lift Machine Room | 20 | Sq.m
Society Input Parameters | Values/Selection | Units | Notes for Values/Selection
FF
FF Pump Set Type | End Suction
UGT FF Set | Separate
FF Standby type | Diesel
Main Pump Flow | 2850 | LPM
Main Pump Head | 99 | Mtr
FF Press. Breat Tank Set | 0
FBT Pump Set Type | Main+SBY+Jky | Nos | As per CFO NOC or NBC whichever is applicable
FBT Pump Flow | 900 | LPM
FF Booster Pump Set | 1 | Nos
FF Booster Pump Flow | 900 | LPM
PHE
UGT DOM Transfer Flow | 200 | LPM
UGT DOM Transfer Head | 99 | Mtr
UGT DOM Transfer Config. | 1W+1S
UGT FLU Transfer Flow | 300 | LPM
UGT FLU Transfer Head | 99 | Mtr
UGT FLU Transfer Config. | 2W+1S
Irrigation Pump Set | 1 | Nos
Irrigation Pump Flow | 150 | LPM
Sump Pump Nos | 3 | Nos | Oil Trap dewatering, STP, UGT, Basement Dewatering pumps etc
Sump Pump Head | 35 | Mtr
Booster Pump Set | 1 | Nos | Terrace DOM Booster, Flushing Booster(If applicable) etc
Booster Pump Flow | 300 | LPM
HVAC & Ventilation
UGT Pump room Area | 200 | Sq.m
STP | 275 | KLD | Assumed that STP Load is metered under separate meter

## Building CA LOAD
S.NO. | Description | Details | Carpet Area in sqm | Carpet Area in sqft | Watt per sqft | Nos. | TCL per unit (KW) | TCL (kW) | MDF | Maximum Demand (KW) | EDF | Essential Demand (KW) | FDF | Fire Demand (KW) | Remarks
1 | Lighting & Small Power | GF Entrnace Lobby | 100 | 1076 | 0.3 | 1 | 0.3228 | 0.3228 | 0.6 | 0.19368 | 0.6 | 0.19368 | 0.25 | 0.0807 | Assumed per EcoNiwas Samhita 3W/sq.m
2 | Lighting & Small Power | Typical Floor lobby | 30 | 322.8 | 0.3 | 38 | 0.09684 | 3.6799 | 0.6 | 2.208 | 0.6 | 2.208 | 0.25 | 0.91998 | Assumed per EcoNiwas Samhita 3W/sq.m
3 | Lighting & Small Power | Staircase |  |  |  | 152 | 0.02 | 3.04 | 0.6 | 1.824 | 0.6 | 1.824 | 1 | 3.04 | 20 Watts per fixtures and calculated based on Number of total Landings for 2 STRs
4 | Lighting & Small Power | Terrace | 800 | 8608 | 0.3 | 1 | 2.5824 | 2.5824 | 0.6 | 1.5494 | 0.6 | 1.5494 | 0.25 | 0.6456
5 | Lighting & Small Power | Fire Lift lobby | 8 | 86.08 | 0.3 | 39 | 0.025824 | 1.0071 | 0.6 | 0.60428 | 0.6 | 0.60428 | 0.25 | 0.25178 | Assumed per EcoNiwas Samhita 3W/sq.m
6 | Lighting & Small Power | Refuge Floor | 90 | 968.4 |  | 5 | 0.38736 | 1.9368 | 0.6 | 1.1621 | 0.6 | 1.1621 | 0.25 | 0.4842 | 20 Watts per fixtures and calculated based 1 fix per 50sq.ft
7 | Lighting & Small Power | Service Floor | 1200 | 12912 | 0.3 | 1 | 3.8736 | 3.8736 | 0.6 | 2.3242 | 0.6 | 2.3242 | 0.25 | 0.9684
8 | Lighting & Small Power | External (Facade) |  |  |  | 1 | 5 | 5 | 0.6 | 3 | 0.25 | 1.25 | 0 | 0 | Assumed per Building Height
9 | Lighting & Small Power | Landscape | 500 | 5380 | 0.8 | 1 | 4.304 | 4.304 | 0.6 | 2.5824 | 0.25 | 1.076 | 0 | 0 | 0.8 W/Sqft for building assosiated Landscapes
10 | Lifts | Passenger Lift |  |  |  | 2 | 15 | 30 | 0.6 | 18 | 0.6 | 18 | 0 | 0 | Lift Motor loads formalized as per height of the building.
10 | Lifts | Passenger + Fire Lift |  |  |  | 1 | 15 | 15 | 0.6 | 9 | 0.6 | 9 | 1 | 15 | 1 Passenger lift converted to Fire lift per lift Bank during Fire as per CFO
11 | Lifts | Firemen Evac/Service/Stretcher Lift |  |  |  | 1 | 15 | 15 | 0.6 | 9 | 0.6 | 9 | 1 | 15
12 | HVAC & Ventilation | Meter Room (Ex Fan) | 15 | 161.4 |  | 3 | 0.7 | 2.1 | 0.6 | 1.26 | 0.6 | 1.26 | 0.6 | 1.26 | Refer Data sheet for details
13 | HVAC & Ventilation | Electrical Room (Ex Fan) | 25 | 269 |  | 1 | 0.9 | 0.9 | 0.6 | 0.54 | 0.6 | 0.54 | 0.6 | 0.54 | Refer Data sheet for details
14 | HVAC & Ventilation | IBS room 1+1 (Ex Fan) | 15 | 161.4 |  | 2 | 0.7 | 1.4 | 0.6 | 0.84 | 0.6 | 0.84 | 0.6 | 0.84 | Refer Data sheet for details
15 | HVAC & Ventilation | OWC Room (Ex Fan) | 50 | 538 |  | 1 | 2.5 | 2.5 | 0.6 | 1.5 | 0.6 | 1.5 | 0 | 0 | Refer Data sheet for details
16 | HVAC & Ventilation | FCC Room (AC) | 30 | 322.8 |  | 2 | 1.6 | 3.2 | 0.6 | 1.92 | 0.6 | 1.92 | 0 | 0 | Refer Data sheet for details
17 | HVAC & Ventilation | Lift Machine Room (AC) | 20 | 215.2 |  | 1 | 1.2 | 1.2 | 0.6 | 0.72 | 0.6 | 0.72 | 0 | 0 | Refer Data sheet for details
18 | HVAC & Ventilation | Lift Machine Room (Ex Fan) | 20 | 215.2 |  | 1 | 0.8 | 0.8 | 0.6 | 0.48 | 0.6 | 0.48 | 1 | 0.8 | Refer Data sheet for details
19 | Pressurization | Typical Floor Lift Lobby (Press. Fan) |  |  |  | 0
20 | Pressurization | Fire Lift Lobby (Press. Fan) |  |  |  | 0
21 | Pressurization | Staircase 1 (Press. Fan) |  |  |  | 0
21 | Pressurization | Staircase 2 (Press. Fan) |  |  |  | 0
22 | Pressurization | Lift Well (Press. Fan) |  |  |  | 2
23 | PHE | Booster Pump |  |  |  | 1 | 2.2 | 2.2 | 0.6 | 1.32 | 0.6 | 1.32 | 1 | 2.2
24 | FF | Booster Pump |  |  |  | 1 | 11 | 11 | 0.6 | 6.6 | 0.6 | 6.6 | 1 | 11

## Society CA LOAD
S.NO. | Description | Details | Carpet Area in sqm | Carpet Area in sqft | Watt per sqft | Nos. | TCL per unit (KW) | TCL (kW) | MDF | Maximum Demand (KW) | EDF | Essential Demand (KW) | FDF | Fire Demand (KW) | Remarks
1 | PHE | UGT Domestic Transfer Pump |  |  |  | 1 | 7.5 | 7.5 | 0.6 | 4.5 | 0.6 | 4.5 | 0.25 | 1.875
2 | PHE | UGT Flushing Transfer Pump |  |  |  | 2 | 9.3 | 18.6 | 0.6 | 11.16 | 0.6 | 11.16 | 0.25 | 4.65
3 | PHE | Irrigation Pump |  |  |  | 1 | 2.2 | 2.2 | 0.6 | 1.32 | 0.6 | 1.32 | 1 | 2.2
4 | PHE | Sump Pump |  |  |  | 3 | 2.2 | 6.6 | 0.6 | 3.96 | 0.6 | 3.96 | 0.25 | 1.65
5 | FF | Main Hydrant Pump |  |  |  | 1 | 110 | 110 | 0.6 | 66 | 0.6 | 66 | 0.25 | 27.5
6 | FF | Main Sprinkler Pump |  |  |  | 1 | 110 | 110 | 0.6 | 66 | 0.6 | 66 | 0.25 | 27.5
7 | FF | Hydrant Jockey |  |  |  | 1 |  | 0 | 0.6 | 0 | 0.6 | 0 | 0.25 | 0
8 | FF | Sprinkler Jockey |  |  |  | 1 |  | 0 | 0.6 | 0 | 0.25 | 0 | 0 | 0
9 | FF | Electric Standby |  |  |  | 1 |  | 0 | 0.6 | 0 | 0.25 | 0 | 0 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 1 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 1 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0.6 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 0 | 0
[8 empty] | 0 | 0.6 | 0 | 0.6 | 0 | 1 | 0 | Refer Data sheet for details
23
24

## Data
Lift Power as per Bldg Height |  |  | Central Toilet Shaft Ventilation Fan Sizes |  |  |  | MEP room AC Sizes based on Sq.ft
Building height | Lift KW |  | Nos of Floors |  |  |  | Room Area (Sq.ft) | TR/Sq.ft | AC TR | AC Nos | AC Total KW
60 | 12 | [5 empty] | 50 | 0.33333 | 1 | 1 | 0.8
70 | 14 | [5 empty] | 100 | 0.66667 | 1 | 1 | 0.8
90 | 15 | [5 empty] | 150 | 1 | 1 | 1 | 0.8
100 | 18 | [5 empty] | 175 | 1.1667 | 1.5 | 1 | 1.2
110 | 20 | [5 empty] | 200 | 1.3333 | 1.5 | 1 | 1.2
120 | 20 | [5 empty] | 225 | 1.5 | 1.5 | 1 | 1.2
130 | 22 | [5 empty] | 250 | 1.6667 | 1.8 | 1 | 1.44
140 | 25 | [5 empty] | 300 | 2 | 1 | 2 | 1.6
150 | 27 | [5 empty] | 350 | 2.3333 | 1 | 2 | 1.6
[7 empty] | 400 | 2.6667 | 1 | 3 | 2.4
Electrical Rooms - Panel Room, Meter room, IBS, OWC etc (12 ACPH) |  |  |  |  | Pressurization Fan for Lift well based on Height
Area (sq.ft) | Room Volume (cu.ft) | CFM @ 12 ACPH | Fan Selection CFM | Fan KW
50 | 516.5 | 103 | 200 | 0.3 | PHE Booster Pump |  | PHE Irrigation Pump |  |  | FF Main Pump (End Suction) |  |  | FF Main Pump (MSMO)
100 | 1033 | 207 | 300 | 0.5 | Flow (LPM) | KW | Flow (LPM) | KW |  | Head (m) | Flow (LPM) | KW | Head (m) | Flow (LPM) | KW
150 | 1549.5 | 310 | 400 | 0.6 | 100 | 0.75 | 60 | 0.75 |  | 75 | 2280 | 75 | 90/150 | 2280 | 0
200 | 2066 | 413 | 500 | 0.7 | 200 | 1.1 | 90 | 1.1 |  | 75 | 2850 | 0 | 90/150 | 2850 | 110
250 | 2582.5 | 517 | 600 | 0.8 | 300 | 2.2 | 150 | 2.2 |  | 75 | 3200 | 0 | 90/150 | 3200 | 0
300 | 3099 | 620.2 | 700 | 0.9 | 400 | 2.2 | 180 | 2.2 |  | 90 | 2280 | 75 | 90/180 | 2280 | 0
350 | 3615.5 | 723.6 | 800 | 1 | [5 empty] | 90 | 2850 | 0 | 90/180 | 2850 | 130
400 | 4132 | 827 | 900 | 1.2 | PHE Sump Pump |  | PHE Transfer Pump |  |  | 90 | 3200 | 0 | 90/180 | 3200 | 150
450 | 4648.5 | 930.4 | 1000 | 1.5 | Head (Mtr) | KW | Flow (LPM) | KW |  | 100 | 2280 | 75 | 120/210 | 2280 | 0
500 | 5165 | 1033.8 | 1200 | 2 | 20 | 1.1 | 100 | 3 |  | 100 | 2850 | 90 | 120/210 | 2850 | 150
550 | 5681.5 | 1137.2 | 1350 | 2.5 | 35 | 2.2 | 150 | 0 |  | 100 | 3200 | 0 | 120/210 | 3200 | 165
600 | 6198 | 1240.6 | 1500 | 3 |  |  | 200 | 7.5 |  | 120 | 2280 | 75
[7 empty] | 300 | 9.3 |  | 120 | 2850 | 110
[7 empty] | 400 | 15 |  | 120 | 3200 | 115 | FF Jockey Pump (Inline)
[7 empty] | 500 | 18 |  | 130 | 2280 | 90 | Head (Mtr) | KW
[10 empty] | 130 | 2850 | 110 | 75 | 5.5
[10 empty] | 130 | 3200 | 0 | 90 | 7.5
[10 empty] | 45 | 2280 | 0 | 100 | 7.5
[10 empty] | 45 | 2850 | 37 | 120 | 7.5
[10 empty] | 45 | 3200 | 37 | 130 | 7.5
[13 empty] | 45 | 3
[10 empty] | Fire Booster Pump |  |  | FF Jockey Pump (MSMO)
[10 empty] | Flow (LPM) | KW |  | Head (Mtr) | KW
[10 empty] | 900 | 11 |  | 90/150 | 7.5
[10 empty] | 450 | 5.5 |  | 90/180 | 9.3
[13 empty] | 120/210 | 9.3

## C1-HVAC (hidden)
CASA 01 - HVAC ELECTRICAL LOAD SHEET
Sl. | Floor Area | Description | AREA | AREA | Height | Ventilation | Air Change | Air Volume | Fan Selection |  |  | Location Equipment | TSP | Dia | Motor | Phase | Total Qty | Total KW
No. |  |  | (Sqmt.) | (Sq.ft.) | (ft) | Type | per hr. | CFM | cfm / fan | RPM | Type |  | (mm) | (mm) | KW | 1/3 Ph | Nos. | Normal | Smoke | REMARKS
BASEMENT VENTILATION
Zone-01
1 | Parking Axial Fan - B1 | FIRE MODE |  |  |  | NF | 6 | 0 | 65000 | 1450 | TUBE AXIAL |  |  |  | 30 | 3-Ph | 2 |  | 60
2 | Parking Axial Fan - B2 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
3 | Parking Axial Fan - B3 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
4 | Parking Axial Fan - B4 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
5 | Parking Jet Fan - B1 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 11 |  | 16.5
6 | Parking Jet Fan - B2 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 11 |  | 16.5
7 | Parking Jet Fan - B3 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 11 |  | 16.5
8 | Parking Jet Fan - B4 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 11 |  | 16.5
1 | Parking Axial Fan - B1 | NORMAL MODE |  |  |  | NF | 6 | 0 | 32500 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
2 | Parking Axial Fan - B2 | NORMAL MODE |  |  |  | NF | 6 | 0 | 27500 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
3 | Parking Axial Fan - B3 | NORMAL MODE |  |  |  | NF | 6 | 0 | 27500 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
4 | Parking Axial Fan - B4 | NORMAL MODE |  |  |  | NF | 6 | 0 | 27500 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
5 | Parking Jet Fan - B1 | NORMAL MODE |  |  |  | NF | 6 | 0 | 2450 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 11 | 6.05
6 | Parking Jet Fan - B2 | NORMAL MODE |  |  |  | NF | 6 | 0 | 2450 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 11 | 6.05
7 | Parking Jet Fan - B3 | NORMAL MODE |  |  |  | NF | 6 | 0 | 2450 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 11 | 6.05
8 | Parking Jet Fan - B4 | NORMAL MODE |  |  |  | NF | 6 | 0 | 2450 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 11 | 6.05
Zone-02
1 | Parking Axial Fan - B1 | FIRE MODE |  |  |  | NF | 6 | 0 | 72000 | 1450 | TUBE AXIAL |  |  |  | 30 | 3-Ph | 2 |  | 60
2 | Parking Axial Fan - B2 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
3 | Parking Axial Fan - B3 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
4 | Parking Axial Fan - B4 | FIRE MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 22 | 3-Ph | 2 |  | 44
5 | Parking Jet Fan - B1 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 20 |  | 30
6 | Parking Jet Fan - B2 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 17 |  | 25.5
7 | Parking Jet Fan - B3 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 17 |  | 25.5
8 | Parking Jet Fan - B4 | FIRE MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 1.5 | 3-Ph | 17 |  | 25.5
1 | Parking Axial Fan - B1 | NORMAL MODE |  |  |  | NF | 6 | 0 | 72000 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
2 | Parking Axial Fan - B2 | NORMAL MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
3 | Parking Axial Fan - B3 | NORMAL MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
4 | Parking Axial Fan - B4 | NORMAL MODE |  |  |  | NF | 6 | 0 | 55000 | 1450 | TUBE AXIAL |  |  |  | 11 | 3-Ph | 2 | 22
5 | Parking Jet Fan - B1 | NORMAL MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 20 | 11
6 | Parking Jet Fan - B2 | NORMAL MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 17 | 9.35
7 | Parking Jet Fan - B3 | NORMAL MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 17 | 9.35
8 | Parking Jet Fan - B4 | NORMAL MODE |  |  |  | NF | 6 | 0 | 3640 | 1450 | JET FAN |  |  |  | 0.55 | 3-Ph | 17 | 9.35
[18 empty] | 239.25 | 556.5
UTILITY - HVAC
1 | C1 FPS+PHE PUMP ROOM | FRESH AIR FAN |  |  |  | NE | 12 | 9391.3747 | 11000 | 1450 | AXIAL FAN |  | 25 | 900 | 3.7 | 3-Ph | 1 | 3.7
|  | FRESH AIR FAN |  |  |  | NE | 12 | 9391.3747 | 5000 | 1450 | AXIAL FAN |  | 25 | 710 | 1.5 | 3-Ph | 1 | 1.5
|  | EXHAUST AIR FAN |  |  |  | NE | 12 | 9391.3747 | 16000 | 1450 | AXIAL FAN |  | 25 | 1000 | 5.5 | 3-Ph | 1 | 5.5
2 | STILT COMMON AREAS | VENTILATION | [6 empty] | - |  | FANS |  | - | - | 2 | 1-Ph | - | 2 |  | OVERALL
3 | STILT COMMON AREAS | AC | [6 empty] | - |  | AC |  | - | - | 7.5 | 1-Ph | - | 9.75 |  | OVERALL
4 | TERRACE | TOILET EXHAUST | [6 empty] | 4000 |  | CABINET FAN |  | 30 | - | 1.1 | 1-Ph | 4 | 4.4 |  | 4W+4S
5 | TERRACE | TOILET EXHAUST | [6 empty] | 1300 |  | CABINET FAN |  | 30 | - | 0.75 | 1-Ph | 4 | 3 |  | 4W+4S
6 | LIFTWELL VENTILATION | VENT FAN | [6 empty] | 500 |  | PROPELLAR FAN |  | - | - | 0.15 | 1-Ph | 0 | 0 |  | FUTURE
[18 empty] | 29.85 | 0
CLUBHOUSE - HVAC
1 | CLUB AMENITY-1 | AC SYSTEM | [6 empty] | 3.0 TR |  | AC |  | - | - | 4 | 1-Ph | 1 | 4 |  | LHS AMENITY
2 | CLUB AMENITY-2 | AC SYSTEM | [6 empty] | 8.5 TR |  | AC |  | - | - | 10.5 | 3-Ph | 1 | 10.5 |  | NEXT TO LHS CLUB
3 | CLUB AMENITY-3 | AC SYSTEM | [6 empty] | 8.5 TR |  | AC |  | - | - | 10.5 | 3-Ph | 1 | 10.5 |  | -
4 | CLUB AMENITY-4 | AC SYSTEM | [6 empty] | 8.5 TR |  | AC |  | - | - | 10.5 | 3-Ph | 1 | 10.5 |  | -
5 | CLUB AMENITY-5 | AC SYSTEM | [6 empty] | 8.5 TR |  | AC |  | - | - | 10.5 | 3-Ph | 1 | 10.5 |  | -
[18 empty] | 46 | 0
MISCELLANEOUS
1 | MISC. LOAD | MISC. LOAD |  |  |  | NE | 12 | 9391.3747 | - | 1450 | - |  | 25 | 900 | 10 | 3-Ph | 1 | 10
C1 - PRESSURIZATION
1 | C1-FIRE LIFT | PRESSURIZATION FAN | [6 empty] | 26000 |  | LIFTWELLL PRESS. |  | 25 | 1000 | 7.5 | 3-Ph | 1 | 0 | 7.5 | FAN AT TERRACE
2 | C1-FIRE STAIRCASE | PRESSURIZATION FAN | [6 empty] | 23000 |  | STAIR PRESS. |  | 25 | 900 | 7.5 | 3-Ph | 1 | 0 | 7.5 | 12F, CLUB LEVEL
3 | C1-NON FIRE STAIRCASE | PRESSURIZATION FAN | [6 empty] | 23000 |  | STAIR PRESS. |  | 25 | 900 | 7.5 | 3-Ph | 0 | 0 | 0 | 12F, CLUB LEVEL
4 | C1-LIFT LOBBY PRESS. | PRESSURIZATION FAN | [6 empty] | 19000 |  | LOBBY PRESS. |  | 25 | 900 | 7.5 | 3-Ph | 1 | 0 | 7.5 | 13F, CLUB LEVEL
[18 empty] | 0 | 22.5
| Grand Total : CASA-1 HVAC | [16 empty] | 325.1 | 579
NOTE 1 - AIR CONDITIONING AND VENTILATION ELECTRICAL LOADS OF INDIVIDUAL RESIDENTIAL UNTIS ARE NOT INCLUDED HERE IN THESE CALCULATIONS
NOTE 2 - LOADS ARE BASED ON THE SD PACKAGE SUBMISSION, AS PER DD STAGE, LOAD MAY VARY
NOTE 3 - AS PER LODHA TEAM'S INSTRUCTION, LIFTWELL PRESSURIZATION CONSIDERED ONLY IN FIREMAN LIFT.

## C1-PHE ELE LOAD (hidden)
PROJECT: Casa 1 BUILDING
SUBJECT : PHE RELATED ELECTRICAL LOAD
| 1 hp = 746 W = 0.746 KW | 0.746 | KW
Sl. No | Description | Location | Flow rate & head | Type of pumps | LOAD /PUMP |  | No of Pumps (One Set) |  | No of Pump sets | Total Working Load in KW
[5 empty] | HP | KW | Working | Stand by
1 | Domestic water lift Pumps to OHT | Basement 4 | 2.5LPS & 160 m | Mono block | #REF! | #REF! | 2 | 1 | 2 | #REF! | Updated ib 15.05.2023 as per PHE team
2 | Filter feed pump for Rain water | Basement 4 | 2 LPS & 35 m | Mono block | #REF! | #REF! | 1 | 1 | 1 | #REF!
3 | De watering lift pumps (Submersible type) for sump1 | Basement 4 | 12 LPS & 25 m | (Submersible type) | #REF! | #REF! | 1 | 1 | 1 | #REF!
4 | De watering lift pumps (Submersible type) for sump2 | Basement 4 | 12 LPS & 25 m | (Submersible type) | 10 | 7.46 | 1 | 1 | 1 | 7.46
5 | De watering lift pumps (Submersible type) in UG sump | Basement 4 | 4 LPS & 25 m | (Submersible type) | #REF! | #REF! | 1 | 1 | 1 | #REF!
6 | Sewage transfer pumps (Submersible type) | Basement 4 | 25 m | (Submersible type) | 1.76 | 1.313 | 1 | 1 | 1 | 1.313
7 | Booster pump for Domestic supply | Terrace | 8 LPS & 30m | Booster | #REF! | #REF! | 1 | 1 | 1 | #REF! | Updated ib 15.05.2023 as per PHE team
8 | Spare - 1 | [8 empty] | 3
9 | Spare - 2 | [8 empty] | 6
10 | OWC | Stilt - lvl |  |  | 12 | 8.952 | 1 | 1 | 1 | 8.952
| Total PHE Load |  |  |  | #REF! | #REF! | 9 | 8 | 9 | #REF!

## ASPI CA- Lighting (hidden)
Floor | Lights |  | Wattage | Total load (W)
| Normal | EM | Normal | Normal | EM
Stilt | 4 | 1 | 15 | 60 | 75
| 15 | 5 | 20 | 300 | 400
1 | 4 | 1 | 15 | 60 | 15
2 | 4 | 1 | 15 | 60 | 15
3 | 4 | 1 | 15 | 60 | 15
4 | 4 | 1 | 15 | 60 | 15
5 | 4 | 1 | 15 | 60 | 15
6 | 4 | 1 | 15 | 60 | 15 |  | 75
7 | 4 | 1 | 15 | 60 | 15
8 | 4 | 1 | 15 | 60 | 15
9 | 4 | 1 | 15 | 60 | 15 | Refuge | [7 empty] | 0.25
|  | 5 | 20 | 0 | 100 | [5 empty] | 23 | 247.572 | 61.893
10 | 4 | 1 | 15 | 60 | 15 | [7 empty] | 0.30364
11 | 4 | 1 | 15 | 60 | 15
12 | 4 | 1 | 15 | 60 | 15
13 | 4 | 1 | 15 | 60 | 15
14 | 4 | 1 | 15 | 60 | 15
15 | 4 | 1 | 15 | 60 | 15
16 | 4 | 1 | 15 | 60 | 15 | Refuge
|  | 5 | 20 | 0 | 100
17 | 4 | 1 | 15 | 60 | 15
18 | 4 | 1 | 15 | 60 | 15
19 | 4 | 1 | 15 | 60 | 15
20 | 4 | 1 | 15 | 60 | 15
21 | 4 | 1 | 15 | 60 | 15
22 | 4 | 1 | 15 | 60 | 15
23 | 4 | 1 | 15 | 60 | 15 | Refuge
|  | 5 | 20 | 0 | 100
24 | 4 | 1 | 15 | 60 | 15
25 | 4 | 1 | 15 | 60 | 15
26 | 4 | 1 | 15 | 60 | 15
27 | 4 | 1 | 15 | 60 | 15
28 | 4 | 1 | 15 | 60 | 15
29 | 4 | 1 | 15 | 60 | 15
30 | 4 | 1 | 15 | 60 | 15 | Refuge
|  | 5 | 20 | 0 | 100
31 | 4 | 1 | 15 | 60 | 15
32 | 4 | 1 | 15 | 60 | 15
33 | 4 | 1 | 15 | 60 | 15
34 | 4 | 1 | 15 | 60 | 15
35 | 4 | 1 | 15 | 60 | 15
36 | 4 | 1 | 15 | 60 | 15
37 | 4 | 1 | 15 | 60 | 15 | Refuge
|  | 5 | 15 | 0 | 75
38 | 4 | 1 | 15 | 60 | 15
39 | 4 | 1 | 20 | 80 | 20
40 | 4 | 1 | 15 | 60 | 15
41 | 4 | 1 | 15 | 60 | 15
42 | 4 | 1 | 15 | 60 | 15
43 | 4 | 1 | 15 | 60 | 15
44 | 4 | 1 | 15 | 60 | 15 | Total
Total Load in kW |  |  |  | 2.9 | 1.585 | 4.485
Floor | Lights |  | Wattage | Total load (W)
| Normal | EM | Normal | Normal | EM
P-6 | 132 | 48 | 20 | 2640 | 960
P-5 | 137 | 48 | 20 | 2740 | 960
P-4 | 132 | 48 | 20 | 2640 | 960
P-3 | 137 | 48 | 20 | 2740 | 960
P-2 | 143 | 48 | 20 | 2860 | 960
P-1 | 118 | 44 | 20 | 2360 | 880 | Total
Total Load in kW |  |  |  | 10.6 | 3.76 | 14.36
[8 empty] | 3.5333 | 3.3333 | 6.8667

## ASPI-UPS Sizing Calculation (hidden)
UPS Sizing calculation for ASPI & Basements
Sr. No. | Details |  | Remark
1 | ASPI 1 common area Emergency Lighting (kW) | 1.585 | Refer "ASPI1 & Basment- Lighting Load"
2 | Basement area Emergency Lighting (kW) | 3.76
3 | FPS & HVAC damper (kW) | 3.36 | Assumed as per no. of power points
| Total Connected Load (kW) | 8.705
| Diversity | 0.8
| Total Demand Load (kW) | 6.964
| Power factor | 0.9
| Total Demand Load (kVA) | 7.7378
| UPS required at 90% Loading | 8.5975
| UPS Selected | 10 kVA

## C1-FF Load (hidden)
Plumbing & Fire Fighting Electrical Loads
S.No | Item | Total Discharge | Working | Standby | Total | Pump Head | Motor Rating | Total Load for all working pumps | Total Power Requirement
|  | (LPM) | (Nos.) | (Nos.) | (Nos.) | (M) | (HP) | (HP) | (KW)
1 | Fire Hydrant Electric Pump - Split Case/End Suction MSMO | 2850 | - | 1 | 1 | 170 | 200 | - | 149.2
2 | Fire Sprinkler Electric Pump - Split Case/End Suction MSMO | 2850 | - | 1 | 1 | 170 | 200 | - | 149.2
3 | Electric Jockey Pump - Hydrant (Verticle Inline) MSMO | 180 | 1 | - | 1 | 170 | 12.5 | 9.33 | -
4 | Electric Jockey Pump - Sprinkler (Verticle Inline) MSMO | 180 | 1 | - | 1 | 170 | 12.5 | 9.33 | -
6 | Booster pump 900 Lpm for hydrant | 900 |  | 2 | 2 | 35 | 12.5 | - | 9.33
| Total Load on Panel | [6 empty] | 19 | 308

## A-FSI (hidden)
version: ASPI+CASA- all partial heights ¦ 2022-12-14
Towers | Tower Nos. | Levels | RCA / LVL | BUA / LVL | FSI / LVL | Levels | FSI Area Sub Total | FSI Area Total | RCA Sub Total | RCA Total | BUA Sub Total | BUA Total |  | Unit type / Bhk | [7 empty] | Unit numbers | [8 empty] | Car parking
| nos |  | sft | sft | sft | nos | sft | sft | sft | sft | sft | sft |  | 2 BHK | 2.5 BHK | 2.5 BHK |  | 3 BHK | 3 BHK | 3.5 BHK | Sub Totals | 2 BHK | 2.5 BHK | 2.5 BHK |  | 3 BHK | 3 BHK | 3.5 BHK | Sub Totals |  | 2 BHK | 2.5 BHK | 3 BHK | 3.5 BHK | Sub Totals
[15 empty] | 806 | 852 |  | 1015 | 1026 | 1130 |  |  | 806 | 852 |  | 1015 | 1026 | 1130
A1 3 BHK + S | 1 | Typ | 4462 | 6319 | 5019 | 30 | 150570 | 168357 | 133860 | 148430 | 189570 | 221165 | [7 empty] | 4 | 4 | 0 | [5 empty] | 120 | 120
| 1 | Refuge | 3078 | 6319 | 3801 | 4 | 15204 |  | 12312 |  | 25276 | [8 empty] | 3 | 3 | 0 | [5 empty] | 12 | 12
| 1 | Ground | 2258 | 6319 | 2583 | 1 | 2583 |  | 2258 |  | 6319 | [8 empty] | 2 | 2 | 0 | [5 empty] | 2 | 2
A2 3 BHK +S | 1 | Typ | 4462 | 6319 | 5019 | 30 | 150570 | 168357 | 133860 | 148430 | 189570 | 221165 | [7 empty] | 4 | 4 | 0 | 0 | 0 | 0 |  | 0 | 120 | 120
| 1 | Refuge | 3078 | 6319 | 3801 | 4 | 15204 |  | 12312 |  | 25276 | [8 empty] | 3 | 3 | 0 | 0 | 0 | 0 |  | 0 | 12 | 12
| 1 | Ground | 2258 | 6319 | 2583 | 1 | 2583 |  | 2258 |  | 6319 | [8 empty] | 2 | 2 | 0 | 0 | 0 | 0 |  | 0 | 2 | 2
A3 3BHK T-SHAPED | 1 | Typ | 4032 | 5382 | 4670 | 30 | 140100 | 155560 | 120960 | 134017 | 161460 | 188370 | [5 empty] | 4 |  |  | 4 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 120
| 1 | Refuge | 3024 | 5382 | 3548 | 4 | 14192 |  | 12096 |  | 21528 | [6 empty] | 3 |  |  | 3 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12
| 1 | Ground | 961 | 5382 | 1268 | 1 | 1268 |  | 961 |  | 5382 | [6 empty] | 1 |  |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1
A4 2.5 BHK | 1 | Typ | 3286 | 4405 | 3754 | 22 | 82588 | 84410 | 72292 | 73892 | 96910 | 101315 |  |  | 2 | 2 |  |  |  |  | 4 | 0 | 44 | 44 | 0 | 0 | 0 | 0 | 88
| 1 | Refuge | 2486 | 4405 | 2770 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 2 |  |  |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | Ground | 1600 | 4405 | 1822 | 1 | 1822 |  | 1600 |  | 4405 |  |  |  | 0 | 2 |  |  |  |  | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2
A5 3BHK LINEAR | 1 | Typ | 4032 | 5284 | 4589 | 20 | 91780 | 100860 | 80640 | 88610 | 105680 | 121532 | [5 empty] | 4 |  |  | 4 | 0 |  |  | 0 | 80 | 0 | 0 | 80
| 1 | Refuge | 3024 | 5284 | 3444 | 2 | 6888 |  | 6048 |  | 10568 | [6 empty] | 3 |  |  | 3 | 0 |  |  | 0 | 6 | 0 | 0 | 6
| 1 | Ground | 1922 | 5284 | 2192 | 1 | 2192 |  | 1922 |  | 5284 | [6 empty] | 2 |  |  | 2 | 0 |  |  | 0 | 2 | 0 | 0 | 2
A6 2.5 BHK | 1 | Typ | 3286 | 4405 | 3754 | 22 | 82588 | 84410 | 72292 | 73892 | 96910 | 101315 |  |  | 2 | 2 |  |  |  |  | 4 | 0 | 44 | 44 | 0 | 0 | 0 | 0 | 88
| 1 | Refuge | 2486 | 4405 | 2770 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 2 |  |  |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 | Ground | 1600 | 4405 | 1822 | 1 | 1822 |  | 1600 |  | 4405 |  |  |  | 0 | 2 |  |  |  |  | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2
Totals | 6 | [6 empty] | 761954 |  | 667271 |  | 954862 | 1.431 | [8 empty] | Overall | 88 | 92 | 0 | 221 | 0 | 268 | 669 | TOTAL ASPI UNITS |  | 180 | 221 | 268 | 669
[22 empty] | Overall | 13.154 | 13.7519 | 0 | 33.0344 |  | 40.0598 |  |  |  | 225 | 442 | 536 | 1203 | TOTAL ASPI CARS
[22 empty] | Phase 1 | 0 | 0 | 0 | 221 |  | 134 | 355
[22 empty] | Phase 1 | 0 | 0 | 0 | 62.2535 |  | 37.7465
C1(9 units) | 1 | Typ | 4860 | 7648 | 5572 | 18 | 100296 | 147809 | 87480 | 126360 | 137664 | 224377 |  | 9 | [7 empty] | 162
| 1 | Refuge | 3780 | 6151 | 4477 | 3 | 13431 |  | 11340 |  | 18453 |  |  | 6 | [7 empty] | 18
| 1 | podium floors | 2700 | 5702 | 3304 | 9 | 29736 |  | 24300 |  | 51318 |  |  | 5 | [7 empty] | 45
| 1 | podium refuge /first** | 1620 | 4647 | 2173 | 2 | 4346 |  | 3240 |  | 9294 |  |  | 3 | [7 empty] | 6
| 1 | amenity floor | 0 | 7648 | 0 | 1 | 0 |  | 0 |  | 7648 |  |  | 0 | [7 empty] | 0
| 1 | Ground | 0 | 7648 | 0 | 1 | 0 |  | 0 |  | 7648 |  |  | 0 | [7 empty] | 0
0
[22 empty] | 0 | [12 empty] | 1035
0
0
C2(13 units) | 1 | Typ | 7020 | 10485 | 8460 | 29 | 245340 | 276000 | 203580 | 230920 | 304065 | 366362 |  | 13 | [7 empty] | 377
| 1 | 1ST FLOOR (1 UNIT LESS) | 6480 | 9872 | 7850 | 1 | 7850 |  | 6480 |  | 9872 |  |  | 12 | [7 empty] | 12
| 1 | Refuge | 4860 | 10485 | 5416 | 4 | 21664 |  | 19440 |  | 41940 |  |  | 9 | [7 empty] | 36
| 1 | Ground | 1420 | 10485 | 1146 | 1 | 1146 |  | 1420 |  | 10485 |  |  | 2 | [7 empty] | 2
C3(13 units) | 1 | Typ | 7020 | 10485 | 8460 | 30 | 253800 | 278455 | 210600 | 232880 | 314550 | 366975 |  | 13 | [7 empty] | 390
| 1 | Refuge | 4860 | 10485 | 5416 | 4 | 21664 |  | 19440 |  | 41940 |  | 0.84037 | 9 | [7 empty] | 36
| 1 | Ground | 2840 | 10485 | 2991 | 1 | 2991 |  | 2840 |  | 10485 |  |  | 4 | [7 empty] | 4
Totals | 4 | [6 empty] | 702264 |  | 590160 |  | 957714 | 1.6228 | [8 empty] | 1083 | TOTAL 2.0 BHK CASA UNITS | [5 empty] | 1083 |  | 1083 |  |  |  | 1083 | TOTAL CASA CARS
** not a full level due to site driveway levels
[21 empty] | Phase 1 | 231
[14 empty] | 250 | 350 | 500 | 630 | <550 (OTHERS) | >550 |  | Sub Totals | 250 | 350 | 500 | 630 | <550 (OTHERS) | 435 |  | Sub Totals
Signet/ Office | 1 | Typ | 19234 | 26568 | 23361 | 10 | 233610 | 494212 | 192340 | 401164.5001 | 265680 | 590369 |  | 10 | 16 | 7 | 12 |  |  |  |  | 99 | 160 | 70 | 120 |  |  |  | 449
|  | Typ with breakout space | 18982 | 27178 | 23982 | 5 | 119910 |  | 94910 |  | 135890 |  |  | 9 | 16 | 7 | 12 |  |  |  |  | 45 | 80 | 35 | 60 |  |  |  | 220
|  | Typical Refuge | 13816 | 26568 | 17037 | 2 | 34074 |  | 27632 |  | 53136 |  |  | 4 | 5 | 7 | 12 |  |  |  |  | 8 | 10 | 14 | 24 |  |  |  | 56
|  | D1 with Refuge | 13324 | 26568 | 16627 | 1 | 16627 |  | 13324 |  | 26568 |  |  | 0 | 5 | 0 | 12 |  |  |  |  | 0 | 5 | 0 | 12 | 0 |  |  | 17
|  | D2(Doctor's) | 18478.5001 | 26568 | 22969 | 1 | 22969 |  | 18478.5001 |  | 26568 |  |  | 8 | 16 | 7 | 12 |  |  |  |  | 8 | 16 | 7 | 12 | 0 |  |  | 43
|  | R3 (Retail) | 19018 | 27348 | 23642 | 1 | 23642 |  | 19018 |  | 27348 |  |  | 6 | 12 |  | 11 | 8 | 3 |  |  | 6 | 12 | 0 | 11 | 8 | 3 |  | 40
|  | R2 (Retail) | 19018 | 27348 | 23642 | 1 | 23642 |  | 19018 |  | 27348 |  |  | 6 | 12 |  | 11 | 8 | 3 |  |  | 6 | 12 | 0 | 11 | 8 | 3 |  | 40
|  | R1 / Ground | 16444 | 27831 | 19738 | 1 | 19738 |  | 16444 |  | 27831 | [6 empty] | 7 | 11 |  |  |  | 0 |  | 0 | 7 | 11 |  | 18
Totals | [28 empty] | 883 | TOTAL COMMERCIAL UNITS
0
0
[35 empty] | 309.05 | 1015.45
[35 empty] | 4 WHP | 2 WHP
Grand Total | [7 empty] | 1958430 |  | 1658595.5 |  | 2502945 | [16 empty] | 883
[34 empty] | Blended | 504.3288 |  | TOTAL COMMERCIAL CARS
Target FSI area | [7 empty] | 2046732.62 | [8 empty] | 0
% | [7 empty] | 95.6857
[14 empty] | 214 |  | 273.5935
Parking | 1 | P4-P11 |  | 58549 |  | 8 |  |  |  |  | 468392 | 949285 |  | 182 |  | 321.6978
|  | P2-P3 |  | 33088 |  | 2 |  |  |  |  | 66176
|  | P1 |  | 32920 |  | 1 |  |  |  |  | 32920 |  |  | 91 |  | 361.7582 | [6 empty] | 110600
|  | P0 |  | 33442 |  | 1 |  |  |  |  | 33442 |  |  | 91 |  | 367.4945 | [6 empty] | 57375
|  | B1 |  | 77275 |  | 1 |  |  |  |  | 77275 | [11 empty] | 22120
|  | B2,B3,B4 |  | 90360 |  | 3 |  |  |  |  | 271080 | [11 empty] | 7560
[14 empty] | 270 |  | 0 | [6 empty] | 11060
Totals | 1 |  |  |  |  | 16 | [9 empty] | 1324.544 | [6 empty] | 6930 | 3400
[12 empty] | #REF! |  |  |  | 264.9088 | [7 empty] | 16444
#REF!
Aspi Club | 1 | G |  | 15000 |  | 1 |  |  |  |  | 15000 | 24300 | [10 empty] | 178114
|  | 1 |  | 9000 |  | 1 |  |  |  |  | 9000
|  | Terrace (mumty) |  | 300 |  | 1 |  |  |  |  | 300
Totals | 1 |  |  |  |  | 3
494212